SolarKeymark-II

Large open EU market for solar thermal products

Deliverable D 15

Calculation procedures based on the EN 15316-4.3

Dominique CACCAVELLI – CSTB

Project co-ordination: ESTIF

30th, July 2007

This project is co-funded by the European Community

Contract n° EIE/05/052/SI2.420194

# INTRODUCTION

The EN 15316-4.3 European standard: Heating systems in buildings — Method for calculation of system energy requirements and system efficiencies — Part 4-3: Heat generation systems, thermal solar systems was adopted in June 2007.

This European Standard gives methods for calculation of the thermal solar system input for space heating and/or domestic hot water requirements and the thermal losses and auxiliary energy consumption of the thermal solar system. The calculation is based on the performance characteristics of the products given in product standards and on other characteristics required to evaluate the performance of the products as included in the system.

A software was developed in the framework of the European SolarKeymark II project on the basis of this calculation method (figure 1). This software makes it possible to calculate the monthly and annual thermal performance of a thermal solar system as well as the energy savings and the quantity of CO2 avoided compared with a conventional system. For the moment, this software doesn’t have a name and we will therefore call it by its CEN reference, i.e. EN 15316.

Figure 1 – EN 15316 Software

This report aims at describing the validation work of this software that has been carried out.

This validation relies on different test cases coming from thermal solar systems having been the subject of a measurement campaign in single-family houses, residential buildings or in the non-residential sector.

# PRESENTATION OF TEST CASES

Several test cases will serve as a basis for this comparison:

- 3 IDHW test cases in single-family houses

- 2 test cases of collective production of solar hot water in residential buildings and in the hotel sector.

These test cases will be described in the following paragraphs.

Note:

For the moment we do not have test cases at our disposal for Solar Comby Systems.

## IDHW in single-family houseS

In order to know the real performance of IDHWs installed in the framework of the Plan Soleil program and in order to quantitatively evaluate the energy benefit effectively obtained and the environmental impact, the CSTB orchestrated and monitored over one year nearly 120 system in four French regions from 2003 to 2005 .

We have selected from among these 120 systems, 3 systems for which we have the totality of the measurement results. The functioning principle of these systems is given in figure 2.

It concerns 3 solar water-heating systems located in Strasbourg (IDHW 1), Cannes (IDHW 2) and Montpellier (IDHW 3).

Figure 2 – Functioning principle of an IDHW

The characteristics of these 3 systems are described in Table 1.

| IDHW 1 | IDHW 2 | IDHW 3 |
| --- | --- | --- |
| Zone H1: Alsace DE DIETRICH Type B 300 Number of people: 4 Collector area (m²): 4.3 Orientation: 0°C to the south. Angle: 32°C to the horizontal. Tank volume (l): 300 Storage: heated room Back up: built-in gas. | Zone H3: PACA GIORDANO Type S99/07/41 Number of people: 4 Area (m²): 6 Orientation: -5°C to the south Angle: 23°C to the horizontal Tank volume (l): 300 Storage: heated room Back up: built-in electric. | Zone H3: Languedoc-Roussillon GIORDANO Type Giorsol 301/1ECH /SPE Number of people: 4 Area (m²): 4 Orientation: 38°C to the south Angle: 20°C to the horizontal Tank volume (l): 200 Storage: heated room Back up: separated electric. |

Table 1: Characteristics of the 3 IDHW

## Collective solar production

The 2 identified test cases have been continuously monitored under the Guarantee of Solar Results (GSR) procedure over several years and therefore consistent results are available.

### "Les Tilleuls" - Carcassone

This first case test applies to a residential apartment building located in Carcassonne (south part of France). Main characteristics of the thermal solar installation are: (figure 3):

- Collector type and manufacturer: Hélio toiture (Giordano)

- Collector area (gross): 87.6 m2

- Solar tank volume: 5,000 litres

- Type of back-up: Gas boiler

- Type of circuit: Forced circulation with external exchanger

The installation is operated all over the year. It has been designed based on the following hypothesis:

  - domestic hot water temperature: 45 (C

  - annual DHW needs: 74434 kWh

  - solar fraction: 47%

  - annual solar production: 400 kWh/m² (of collector)

Simulation data and results are reported in the annex.

Note:

The simulation has been performed with a 400 m insulated domestic hot water circulation loop with 19 mm of Armaflex and a water flow rate of 400 l/h.

Figure 3 – Carcassone – Solar collective production

### Hotel Novotel - Sophia Antipolis

This second case test applies to a hotel building located in Sophia Antipolis near Nice (south part of France). Main characteristics of the thermal solar installation are: (figure 4):

- Collector type and manufacturer: C8/8s (Giordano)

- Collector area (gross): 113.4 m²

- Solar tank volume: 2 tanks of 3,000 litres each

- Type of back-up: electricity

- Type of circuit: Forced circulation with external exchanger

The installation is operated all over the year. It has been designed based on the following hypothesis:

  - domestic hot water temperature: 60 (C

  - annual DHW needs: 185 112 kWh

  - solar fraction: 50%

  - annual solar production: 810 kWh/m² (of collector)

Simulation data and results are reported in the annex.

Notes:

- The starting of the electric back up is done in the off-peak hours of EDF (French electricity supplier) tariffs, i.e. from 10 pm to 6 am and all day on Sunday.

- The simulation has been performed assuming a 780 m (8 m per room for 97 rooms) domestic hot water circulation loop insulated with 19 mm of Armaflex and a water flow rate of 970 l/h.

Figure 4 – Sophia-Antipolis – Solar collective production

# COMPARISON OF RESULTS

We have compared the simulated results from the EN 15316 software with the experimental results in our possession. Results of the comparison for each test case are listed in table and graph. More detailed results are given in the annex.

## IDHW in single-family houses

The 3 test cases presented in paragraph 2.1 have been simulated with the EN 15316 software. The results of these simulations are reported in tables 2 and 3. The comparison of these results is only done on the level of solar production (figure 5).

|  | EN 15316 | MEASURES |
| --- | --- | --- |
| IDHW 1 | 1279 | 1385 |
| IDHW 2 | 1980 | 1759 |
| IDHW 3 | 671 | 570 |

Table 2 - Results of the simulations in terms of annual solar production (in kWh)

|  | EN 15316 | MEASURES |
| --- | --- | --- |
| IDHW 1 | -8% | 1385 |
| IDHW 2 | 13% | 1759 |
| IDHW 3 | 18% | 570 |

Table 3 - Difference between simulations and measurements in %

Figure 5 - Comparison of the annual solar production of the 3 IDHW with measurements

The EN 15316 software predicts accurate results in terms of annual thermal performance for the first two systems, but less good for the last. That might be explained because the domestic hot water needs of the n(3 configuration are low and therefore the solar production is also low whence a more significant relative difference.

We have reported in Figure 6 for test case n( 1 the calculated and monthly variations of this thermal performance.

Figure 6 - Comparison of the monthly solar production (in kWh) of the IDHW n° 1

We can observ that the EN 15316 software tends to underestimate the monthly variation of solar system performance which means that in fact the real performance of the system is better than that calculated. In the EN 15316 software, a lot of data is given by default and generally these values are penalizing.

## Collective solar production

We have compared the results predicted by the EN 15316 software with the measurement results on the two collective solar hot water systems. These results are presented in table 2 and figure 7 for the Carcassone system and table 3 and figure 8 for the Sophia Antipolis hotel.

|  | EN15316 | MEASURES |
| --- | --- | --- |
| Janury | 209 | 1922 |
| February | 942 | 2427 |
| March | 2284 | 3646 |
| April | 2553 | 2954 |
| May | 2978 | 3437 |
| June | 3213 | 2965 |
| July | 3333 | 2843 |
| August | 3078 | 2957 |
| September | 2874 | 3245 |
| October | 2365 | 2194 |
| November | 881 | 1937 |
| décember | 216 | 1455 |
| Annual | 24927 | 31982 |
| Diff./measures | - 22 % |  |

Table 2 - Results of the monthly comparison of solar production (in kWh)
between EN 15316 and measurements – Carcassonne test case

Figure 7 - Comparison of the solar production (in kWh)
between EN 15316 and Measurements – Carcassonne test case

|  | EN15316 | MESURES |
| --- | --- | --- |
| Janury | 4309 | 2813 |
| February | 4652 | 4680 |
| March | 6417 | 5236 |
| April | 7242 | 7755 |
| May | 7998 | 6725 |
| June | 8308 | 8382 |
| July | 9068 | 9242 |
| August | 9541 | 8946 |
| September | 7584 | 6966 |
| October | 5924 | 4417 |
| November | 4185 | 2639 |
| décember | 369 | 2149 |
| Annual | 78919 | 69950 |
| Diff./mesures | + 13 % |  |

Tableau 3 - Results of the monthly comparison of solar production (in kWh)
between EN 15316 and measurements – Sophia Antipolis test case

Figure 8 - Comparison of the solar production (in kWh)
between EN 15316 and Measurements – Sophia Antipolis test case

For the two collective systems, the recorded differences, between simulations and the measurements, are of ± 20% which is absolutely acceptable taking into account the measurement uncertainties.

# CONCLUSION

The EN 15316 software has been developed in the framework of the European SolarKeymark II project on basis of the calculation method described in the European standard EN 15316-4.3. This software makes it possible to calculate the monthly and annual thermal performance of a thermal solar system as well as the energy savings and the quantity of CO2 avoided compared with a conventional system.

A study was carried out in order to compare the results produced by this software with the experimental data from test cases listed by the CSTB.

These test cases are representative of those that can be found in Europe in the domain of individual and collective solar hot water production.

The results vary depending on the case, but overall the EN 15316 software reproduces in a correct way the behaviour of the solar system knowing that the experimental data are also subject to caution and that is concerns a very simplified calculation method.

This software can therefore be used as a calculation tool in order to promote in Europe the development of thermal solar systems.

ANNEX

Detailed reports for simulation

EN 15316

# IDHW 1

# IDHW 2

# IDHW 3

# CARCASSONE

# NOVOTEL SOPHIA ANTIPOLIS

# Footnotes

Carol Buscarlet – Dominique Caccavelli

Monitoring of 120 solar DHW systems in France

3rd European Solar Thermal Energy Conference (ESTEC 2007)

Fribourg, June 2007 – pp 203-207